## Sheet1
Yearly Range | Dry or Wet Bulb | Jan | Feb | Mar | Apr | May | Sep | Oct | Nov | Dec
32°C | Dry-Bulb | 0 | 0 | -1 | -3 | -6 | -4 | -4 | -2 | 0 |  | Surfaces |  | R-value(m^2°C/W) | U-value(W/m^2°C)
| Wet-Bulb | 0 | 0 | 0 | -1 | -2 | -2 | -2 | 0 | 0 |  | Floor |  | 0.725 | 1.38
[12 empty] | Ceiling | T.0.6 | 2.496 | 0.401
[13 empty] | MM.0.3 | 1.7 | 0.588
Design condition | External conditons | Jan: Internal conditons |  | External Wall |  | W: 0.5055 | W: 1.978
|  | Jan: T.0.6; Feb: M.0.3 |  |  |  | S: 0.5085 | S: 1.967
Summer | 33.8°C DB/22.9°C WB | Jan: 23.5°C DB/55%RH; Feb: 23.5°C DB/55%RH |  | Internal Wall |  | 0.562 | 1.78
Winter | 2.1°C DB/80%RH | Jan: 21°C DB/80%RH; Feb: 21°C DB/80%RH
[12 empty] | Surfaces |  | R-values(m^2°C/W) | Increment of Insulation(m^2°C/W) | Corrected R-values | Corrected U-values
Surfaces | R-value(m^2°C/W) | Jan: U-value(W/m^2°C) |  | Floor |  | 0.725 | 1 | 1.725 | 0.57971
Floor | 0.725 | Jan: 1.38 |  | Ceiling | T.0.6 | 2.496 | 1 | 3.496 | 0.28604
Ceiling | [12 empty] | MM.0.3 | 0.588 | 3 | 3.588 | 0.27871
External Wall | W: 0.5055 | Jan: W: 1.978 |  | External Wall |  | W: 0.5055 | 2 | 2.5055 | 0.39912
| S: 0.5085 | Jan: S: 1.967 |  |  |  | S: 0.5085 | 2 | 2.5085 | 0.39864
Internal Wall | 0.562 | Jan: 1.78 |  | Internal Wall |  | 0.562 | 0.5 | 1.062 | 0.94162
Component | Thickness (mm) | Jan: R-values (m^2℃/W ); Feb: References
Metal deck | / | Jan: 0; Feb: Table37 Page81 DA09
Wood deck | 25 | Jan: 0.165; Feb: Table37 Page82 DA09
Wood rafter | 100 | Jan: 0.722; Feb: Table37 Page82 DA09
Fiberglass | 100 | Jan: 3.15; Feb: Table37 Page79 DA09
Plaster | 15 | Jan: 0.041; Feb: Table37 Page78 DA09
storage mass | ceiling
Shop T.0.6
Component | Thickness (mm) | Jan: Density; Feb: Mass perunit area (Kg/m2); Mar: Area (m2); Apr: Mass (kg)
Metal deck | 30 | Jan: 78.5; Feb: /; Mar: 146; Apr: 343.83
Wood deck | 25 | Jan: 106; Feb: /; Mar: 146; Apr: 386.9
Wood rafter&fibreglass | 100 | Jan: 177.89; Feb: /; Mar: 146; Apr: 2597.194
Plaster | 15 | Jan: 1121; Feb: /; Mar: 146; Apr: 2454.99
Batts*2 | 150 | Jan: 32; Mar: 146; Apr: 700.8
Total mass (kg) |  | Apr: 6483.714
MM.0.3
Component | Thickness (mm) | Jan: Density; Feb: Mass perunit area (Kg/m2); Mar: Area (m2); Apr: Mass (kg)
Bituminous felt roof with 150mm of concrete and 25 mm of sand and cement topping and plaster tiles | 187 | Jan: /; Feb: 437; Mar: 440; Apr: 192280
Batts*6 | 450 | Jan: 32; Feb: /; Mar: 440; Apr: 6336
Total mass (kg) |  | Apr: 198616
Floor Shop T.0.6
Component | Thickness (mm) | Jan: Density; Feb: Mass perunit area (Kg/m2); Mar: Area (m2); Apr: Mass (kg)
100mm concrete with + 25mm sand/topping + carpet and underlay | 125 | Feb: 287; Mar: 146; Apr: 41902
Batts*2 | 150 | Jan: 32; Mar: 146; Apr: 700.8
Total mass (kg) |  | Apr: 42602.8
MM.0.3
Component | Thickness (mm) | Jan: Density; Feb: Mass perunit area (Kg/m2); Mar: Area (m2); Apr: Mass (kg)
100mm concrete with + 25mm sand/topping + carpet and underlay | 125 | Jan: /; Feb: 287; Mar: 440; Apr: 126280
Batts*2 | 150 | Jan: 32; Mar: 440; Apr: 2112
Total mass (kg) |  | Apr: 128392
External wall
T06
Component | Thickness (mm) | Jan: Density; Feb: Mass perunit area (Kg/m2); Mar: Area (m2); Apr: Mass (kg)
2×90mm brick with 60mm air gap | 240 | Jan: /; Feb: 346; Mar: 45; Apr: 15570
Plaster | 15 | 1121 | / | 45 | 756.675 |  |  | t06,N | MM03
Marble | 20 | 2700 | / | 45 | 2430 |  | N | 9 | 20 |  | 90 | 30
Batts*4 | 300 | 32 | / | 45 | 432 |  | E |  | 26 |  | 117 | 39
Total mass (kg) |  | Apr: 19188.675; May: 426.415; Sep: Window; Oct: 3*3; Nov: 1.5h | 1218.6383
MM.0.3
Component | Thickness (mm) | Density | Mass perunit area (Kg/m2) | Area (m2) | Mass (kg) |  |  | 45 | 207 |  | 5702.6
2×90mm brick with 60mm air gap | 240 | Jan: /; Feb: 346; Mar: 207; Apr: 71622; Nov: 69 | 8890.0497
Plaster | 15 | Jan: 1121; Feb: /; Mar: 207; Apr: 3480.705
Marble | 20 | Jan: 2700; Feb: /; Mar: 207; Apr: 11178
Batts*4 | 300 | Jan: 32; Feb: /; Mar: 207; Apr: 1987.2
Total mass (kg) |  | Apr: 88267.905
Internal wall |  | May: 426.415; Oct: 246
Component | Thickness (mm) | Jan: Density; Feb: Mass perunit area (Kg/m2); Mar: Area (m2); Apr: Mass (kg)
12mm plaster board + 100mm + 12mm plaster board | 124 | Feb: 11; Mar: 246; Apr: 2706
Component | Thickness (mm) | Jan: Density; Feb: Mass perunit area (Kg/m2); Mar: Area (m2); Apr: Mass (kg)
12mm plaster board + 100mm + 12mm plaster board | 124 | Feb: 11; Mar: 276; Apr: 3036; Oct: 46; Nov: 276
Solar Transmission
Heat Load for External Surface | bar: Jan
Room | Summer(W) | Jan: Winter(W)
T.0.6 | 884.4 | Jan: -1295.3
MM.0.3 | 5702.6 | Jan: -8890.1
Heat load for external surface (MM.0.3)
| Summer | Jan: Winter
Total
Equipment load
MM.0.3 | bar: Jan to Feb
Equipment | number | Jan: Sensible(W); Feb: Laternt(W)
Coffee machine 5L | 1 | Jan: 2500; Feb: 1100
Microwave oven | 1 | Jan: 1400; Feb: 0
Toaster | 1 | Jan: 655; Feb: 580
Desktop computer | 1 | Jan: 180; Feb: 0
Laptop computer | 1 | Jan: 32.5; Feb: 0
Flat-panel monitor 15'' | 5 | Jan: 95; Feb: 0
Flat-panel monitor 30'' | 10 | Jan: 900; Feb: 0
Flat-panel monitor 45'' | 15 | Jan: 1635; Feb: 0
Flat-panel monitor 60'' | 10 | Jan: 1800; Feb: 0
Cash register | 4 | Jan: 192; Feb: 0
|  | 9389.5 | 1680
Internal cooling load in summer | bar: Jan to Mar
Division | T.0.6 | Feb: MM.0.3
| Sensible(W) | Jan: Latent(W); Feb: Sensible(W); Mar: Latent(W)
People | 3240 | Jan: 2610; Feb: 9072; Mar: 7308
Equipment | 2542 | Jan: 300; Feb: 9390; Mar: 1680
Lights | 4803 | Jan: 0; Feb: 12144; Mar: 0
Infiltration | 4728 | Jan: 3328; Feb: 11970; Mar: 7721
Total | 15313 | Jan: 6238; Feb: 42576; Mar: 16709
Internal heating load in winter | bar: Jan to Mar
Division | T.0.6 | Feb: MM.0.3
| Sensible(W) | Jan: Latent(W); Feb: Sensible(W); Mar: Latent(W)
People | 0 | Jan: 0; Feb: 0; Mar: 0
Equipment | -300 | Jan: 0; Feb: 0; Mar: 0
Lights | 0 | Jan: 0; Feb: 0; Mar: 0
Infiltration | 8675 | Jan: 9383; Feb: 20129; Mar: 23164
Total | 8375 | Jan: 9383; Feb: 20129; Mar: 23164
Cooling Load in Summer | bar: Jan to Mar
Load Type | T.0.6 | Feb: MM.0.3
| Sensible | Jan: Latent; Feb: Sensible; Mar: Latent
External Load | 909 | Jan: 0; Feb: 5878; Mar: 0
Internal Load | 15313 | Jan: 6238; Feb: 42576; Mar: 16709
Total | 16222 | Jan: 6238; Feb: 48454; Mar: 16709
Heating Load in Winter | bar: Jan to Mar
Load Type | T.0.6 | Feb: MM.0.3
| Sensible | Jan: Latent; Feb: Sensible; Mar: Latent
External Load | 1295 | Jan: 0; Feb: 8890; Mar: 0
Internal Load | 8375 | Jan: 9383; Feb: 20129; Mar: 23164
Total | 9670 | Jan: 9383; Feb: 29019; Mar: 23164
Load Type |  | Jan: Camel; Mar: Hand Calculation
|  | T06 | MM03 | T06 | MM03
Summer | Sensible | Jan: 16602; Feb: 53414; Mar: 16222; Apr: 48545
| Latent | Jan: 6741; Feb: 17950; Mar: 6903; Apr: 18254
Winter | Sensible | Jan: 10896; Feb: 31850; Mar: 9634; Apr: 12017
T.0.6 |  | Jan: CAMEL; Mar: Hand Calculation
|  | Sensible | Latent | Sensible | Latent
External | Wall | Jan: 94; Feb: 0; Mar: 140; Apr: 0
| Radiation | Jan: 572; Feb: 0; Mar: 248; Apr: 0
| Glass | Jan: 521; Feb: 0; Mar: 521; Apr: 0
Internal | People | Jan: 3600; Feb: 2900; Mar: 3240; Apr: 2610
| Appliances | Jan: 2500; Feb: 300; Mar: 2542; Apr: 300
| Lights | Jan: 4408; Feb: 0; Mar: 4803; Apr: 0
| Infiltration | Jan: 4776; Feb: 3541; Mar: 4728; Apr: 3328
Total |  | Jan: 16471; Feb: 6741; Mar: 16222; Apr: 6238
MM.0.3 |  | Jan: CAMEL; Mar: Hand Calculation
|  | Sensible | Latent
External | Wall | Jan: 626; Feb: 0; Mar: 739; Apr: 0
| Radiation | Jan: 8135; Feb: 0; Mar: 1219; Apr: 0
| Glass | Jan: 3995; Feb: 0; Mar: 3994; Apr: 0
Internal | People | Jan: 10080; Feb: 8120; Mar: 9072; Apr: 7308
| Appliances | Jan: 9400; Feb: 1700; Mar: 9390; Apr: 1680
| Lights | Jan: 10602; Feb: 0; Mar: 12144; Apr: 0
| Infiltration | Jan: 10967; Feb: 8130; Mar: 11970; Apr: 7721
Total |  | Jan: 53805; Feb: 17950; Mar: 48528; Apr: 16709
Heating load
Load Type | camel | Feb: hand calculation
| T06 | Jan: MM03; Feb: T06; Mar: MM03
sensible | 10896 | Jan: 31850; Feb: 9670; Mar: 29019
latent | / | Jan: /; Feb: 9383; Mar: 23164